产品标题：ZW32-24 (G) outdoor high voltage vacuum circuit breaker

短描述：

ZW32-24(G) series outdoor high-voltage vacuum circuit breaker (hereinafter referred to as circuit breaker) is a three-phase AC 50Hz, rated voltage 24kv outdoor switchgear, suitable for opening and closing various load currents and frequent operation occasions, suitable for power equipment construction and transformation of urban grid, rural grid, mine and railway. Compared with similar products, this product has the characteristics of miniaturization, maintenance-free and intelligent. In recent years, with the continuous expansion of urban power grids and the rapid growth of power load in my country, and the characteristics of long power supply lines and large line losses in rural power grids, the original 10kV voltage level distribution has been difficult to meet the power supply requirements, and gradually exposed its weaknesses such as too long power supply distance, high line loss rate, and voltage quality that is difficult to meet the requirements. The use of 24kv voltage level power supply has a series of advantages such as increasing power supply capacity, ensuring voltage quality, reducing power grid power loss, and saving power grid construction costs.

The circuit breaker complies with technical standards such as GB1984-2003 High Voltage AC Circuit Breaker and DLT402-2007 High Voltage AC Circuit Breaker Ordering Technical Conditions and DL/T403-2000 12kV~40.5kV High Voltage Vacuum Circuit Breaker Ordering Technical Conditions.

详情内容：

Usage Environment

·Ambient air temperature: upper limit +40℃, lower limit -40℃;

·Relative humidity of air: daily average value is not more than 95%, monthly average value is not more than 90%;

·Altitude: ≤ 3000mm;

·Wind pressure: no more than 700Pa (equivalent to wind speed 34m/s);

·Pollution level: Ⅳ Level [creepage distance> 31mm/kV;

·Ice thickness: ≤ 10mm;

·Installation location: There should be no fire, explosion hazard, serious pollution, chemical corrosion and severe vibration, etc.

Structural features

◆The shell is made of high-quality stainless steel or ordinary steel plate through Dacromet anti-rust treatment process and then sprayed with UV-resistant varnish. The product has excellent anti-corrosion, anti-salt spray and other environmental resistance properties.

◆APG sealed insulation pole is encapsulated with silicone rubber (as insulation and buffer 1, small size, excellent anti-dew performance, long working life and reliable performance.

◆The operating mechanism is a spring operating mechanism, which is available in manual and electric versions. A remote control device and a device to avoid inrush current when closing the switch can be installed when necessary. The required external power supply power is no more than 70W, and it is easy to equip a backup power supply. The uniquely designed buffer device has excellent performance, small rebound and low noise.

◆The arc extinguishing chamber adopts special stainless steel brazing technology, which does not require electroplating, has high welding quality, is stable and reliable, and has a low leakage rate. The production process uses a special ceramic metallization formula and ceramic metallization process to ensure the airtightness of the product, with a tensile strength greater than 130Mpa, and is completely sealed once.

◆The current transformer is made of high-quality magnetic conductive material and epoxy resin and silicone rubber composite insulation. It has the advantages of large capacity, high dynamic thermal stability, high precision, maintenance-free and high reliability.

◆According to user needs, it can be combined with corresponding controllers to form automatic reclosers and sectionalizers, which are equipment for realizing distribution network automation.

Technical Parameters

| Serial number | Name |  | Unit | Data |  |
| --- | --- | --- | --- | --- | --- |
| 1 | Rated voltage |  | kV | 24 |  |
| 2 | Rated frequency |  | HZ | 50 |  |
| 3 | Rated current |  | A | 630 | 1250 |
| 4 | Rated short-circuit breaking current |  | kA | 20 | 25 |
| 5 | Rated peak withstand current (peak) |  | kA | 50 | 63 |
| 6 | Rated short-circuit making current （peak value) |  | kA | 50 | 63 |
| 7 | Rated short-time withstand current/duration |  | KA/s | 20\4 | 25\4 |
| 8 | Rated operating sequence |  |  | 0-0.3s-CO-180s-CO |  |
| 9 | Mechanical life |  | Second-rate | 10000 |  |
| 10 | Rated short-circuit breaking current breaking times |  | Second-rate | 20 |  |
| 11 | 1min power frequency withstand voltage | (Wet test) phase to phase, to ground/break | kV | 50/65 |  |
|  |  | (Dry test) phase to phase, to ground/break |  | 65/79 |  |
|  |  | Secondary circuit |  | 2 |  |
| 12 | Lightning impulse withstand voltage (peak) between phases, to ground/break |  | kA | 125/145 |  |
| 13 | weight |  | kg | 115 |  |

Appearance and installation dimensions